DIVISION 08 - OPENINGS

SECTION 08 42 43 – INTERMEDIATE / INTENSIVE / CRITICAL CARE UNIT ENTRANCES

Specifier Note: Coordinate and edit articles and paragraphs below to suit project requirements. Add section numbers and titles per CSI "MasterFormat" and specifier's practice. Consult with manufacturer regarding performance requirements for units applicable to project, as well as, related equipment and accessories required.

PART I – GENERAL

1.01 SUMMARY

A. 	WORK INCLUDED: Furnish specified manual door system that has been manufactured, fabricated & installed to meet manufacturer’s standards without defects, damage or failure.

B. 	RELATED WORK: Openings: Division 08, applicable sections.

1.02 REFERENCES

A. 	THE ALUMINUM ASSOCIATION (AA) Aluminum Finishes Manual.

B.	AMERICAN ARCHITECTURAL MANUFACTURERS ASSOCIATION (AAMA) 101: Dissimilar Materials.

C. 	AMERICAN NATIONAL STANDARDS INSTITUTE

1.	ANSI A117.1 Standard for Accessible and Usable Buildings and Facilities

2. 	ANSI A156.5: Standard for Auxiliary Locks and Associated Products

3. 	ANSI A156.18: Standard for Materials and Finishes

D. 	AMERICAN SOCIETY FOR TESTING AND MATERIALS (ASTM) B221: Aluminum-Alloy Extruded Bars, Rods, Shapes and Tubes.

E. 	ARCHITECTURAL WOODWORK STANDARDS (AWS): Specification for the fabrication, finishing, and installation of architectural woodwork.

E. 	NATIONAL FIRE PROTECTION ASSOCIATION (NFPA) 101: Safety to Life from Fire in Buildings & Structures.

F. 	INTERTEK, WARNOCK HERSEY (ETL): Testing Laboratory and Certification Agency joined with ETL SEMKO

1.03 SUBMITTALS

A. 	SHOP DRAWINGS & PRODUCT DATA: Submit drawings and product data showing layout, profiles, product components including anchorage, accessories, finish and glazing details (where required).

B. 	CLOSEOUT SUBMITTALS: Submit Owner’s Manual & Warranty document as specified herein.

1.04 QUALITY ASSURANCE

A. 	INSTALLERS QUALIFICATIONS: Installer experienced to perform work of this section who has specialized in the installation of work like that required for this project and who is acceptable to product manufacturer.

B. 	MANUFACTURER’S QUALIFICATIONS: Manufacturer to have minimum (5) five years successful experience in the fabrication of intensive/critical care doors of the type required for this project. Manufacturer to provide field service representation during installation, approving acceptable installer and approving application method.

C.	CERTIFICATIONS: Manual sliding door systems to be certified in accordance with NFPA 105.

D.	OPENING FORCE REQUIREMENT: Shall be 5 lbs. or less for standard wood door. Note: Selection of self-closing mechanism and/or alternative seal options may increase opening force.

E.	HEADER CAPACITY: Up to 200 lbs. (90.7 kg) per slide panel.

1.05 WARRANTIES

A. 	MANUFACTURER'S WARRANTY: Units to be warranted against defect in material and workmanship for a period of one year from the Date of Substantial Completion. Manufacturer's warranty is in addition to, and not a limitation of, other rights owner may have under Contract Documents.

B. 	DISTRIBUTOR'S WARRANTY: 1-year warranty: Labor & transportation charges for defective parts replacement.

1.06 PROJECT CONDITIONS

Field Measurements: Verify actual dimensions/openings by field measurements before fabrication and record on shop drawings. Coordinate with fabrication and construction schedule to avoid construction delays.

1.07 DELIVERY, STORAGE AND HANDLING

A. 	ORDERING AND DELIVERY: Comply with factory's ordering instructions and lead time requirements. Delivery shall be in factory's original, unopened, undamaged containers with identification labels intact.

B. 	STORAGE AND PROTECTION: Provide protection from exposure to harmful weather conditions and vandalism.

# PART II – PRODUCTS

2.01 MANUFACTURER

Horton Automatics, a division of Overhead Door Corporation, shall manufacturer manual slide door(s) of type(s) and size(s) specified on plans and door schedule.

2.02 EQUIPMENT

A.	MANUFACTURED DOOR UNITS: Includes header with roller track, carrier assemblies with interlocked valance framing system, concealed floor guide(s), slide door panel(s), and accessories required for complete installation.

1.  Configuration: Single Slide or Biparting.

2. 	Mounting Type: Drywall cased with interlocked header on exterior.

3. 	Door Types: Type 010 P-X, X-P & P-X-X-P: Slide panel(s) ‘X’ slide along wall utilizing concealed floor mounted guide.

4. Minimum Clear Slide Opening Widths:

a. 	36” (914mm) for Single Slide

b. 	52” (1321mm) for Biparting

B. HEADER: To be aluminum with double top track & removable faceplate and integral end caps. Header to be interlocked with valance frame and located on exterior side with no exposed fasteners. Header size to be

2 7/8” (73mm) deep by 4" (102mm) high. Biparting units (P-X-X-P) shall incorporate door synchronizing mechanism that allows for simultaneous opening of door panels. Header options shall be:

- Soft Opening Dampening: approximately 6” (152mm) from Full‐Open, switch engages internal spring to auto open door to Full‐Open.

- Soft Closing Dampening: approximately 6” (152mm) from Full‐Close, switch engages internal spring to auto close door to Full‐Close.

- Soft Opening and Soft Closing Dampening Combination

- Spring Retractor Self-Closing Mechanism

C. CARRIER ASSEMBLIES AND HEADER ROLLER TRACK: Double track system shall be integral part of header.

Tracks shall be 1/4" (6mm) wide. Rollers will be steel, high quality ball bearing wheels 1 1/8" (29mm) diameter. Anti-Derailing accomplished by means of a continuous aluminum extrusion full length of slide panel travel.

D. 	SLIDE PANEL(S): Shall be wood veneered door with structural composite lumber core with 5-ply (SCLC-5) construction.

1. 	Optional Sliding Panel(s) shall be:

a.	Plastic laminated door with High-Pressure Decorative Laminates (HPDL) and structural composite lumber core with 5-ply (SCLC-5) construction.

b.	Wood door panel by others.

2. Locking Hardware: shall be provided as follows:

a.  Single Slide Units: Shall be provided with positive latch that will latch the panel in place when closed.       A lever handle shall be provided on each side of the sliding panel to unlock the door along with interior thumb-turn and exterior key-turn lock.

b. 	Biparting Units: Shall be provided with interior thumb-turn and exterior key-turn lock. Each slide panel shall be provided with a raised 1” (25mm) diameter tubular pull.

3. Optional Locking Hardware:

a.  Flush Turn - Key one side or both sides

b.	Lever handle only or with key both sides

c.	Lever handle – ADA Turn/Key

d.	ADA LaviLock – Left Hand or Right Hand

e.	ADA Indicator – Left Hand or Right Hand

f.	ADA Magnetic Privacy Lock

g.	Raised 1” (25mm) diameter tubular pull only

4. Optional Acoustic drop-down seals for single slide panel widths 42 1/2” up to 48 1/2”.

E. 	VALANCE CASED FRAME: Shall be aluminum with no exposed fasteners with miter corner joints and interlocked with header. Two-piece overlapping casement frame shall be 2” (51mm) wide with adjustable casement depth of 5” (129mm) to 8” (203mm).

2.03 MATERIALS, FINISHES AND FABRICATION

A. 	EXTRUDED ALUMINUM: ASTM B221, 6063-T5 alloy and temper, anodized:

1. 	Structural Header Sections: Minimum 3/16" (5mm) thickness.

2. 	Structural Frame Sections: Commercial grade.

B. 	FINISHES (for all exposed aluminum surfaces): Shall be one of the following with optional antimicrobial coating:

1. 	215-R1 Clear: Architectural Class 1 Clear Anodized Coating, AA-MI2C22A41.

2. 	313-R1 Dark Bronze, 312-R1 Light Bronze, or 315-R1 Black: Architectural Class 1 Anodized Coating,        AA-MI2C22A44.

3. 	Special Powder-coat Paint Coating: Color as selected.

4. 	Antimicrobial coating.

C. 	FRAME CONSTRUCTION: Drywall cased open framing system with no exposed fasteners.

PART III - EXECUTION

3.01 EXAMINATION

Site Verification of Conditions: Installer shall verify base conditions are acceptable for product installation as per manufacturer's instructions. Notify Contractor in writing of conditions detrimental to proper & timely completion of work. All negative conditions to be corrected in a manner acceptable to the manufacturer.

3.02 INSTALLATION

A. 	GENERAL: Install door units plumb, level and true to line, without warp or rack of frames or sash with manufacturer's prescribed tolerances. Provide support and anchor in place.

B. 	DISSIMILAR MATERIALS: Comply with AAMA 101, Appendix Dissimilar Materials by separating aluminum materials and other corrodible surfaces from sources of corrosion or electrolytic action contact points.

3.03 CLEANING, ADJUSTMENT AND PROTECTION

A. 	CLEANING AND ADJUSTEMENT: Remove temporary protection of adjacent work areas. Remove construction debris from construction site and legally dispose of debris. Repair or replace damaged installed products. Clean product surfaces and lubricate operating equipment for optimum condition and safety

B. 	ADVISE CONTRACTOR: Of precautions required through the remainder of the construction period, to ensure that doors will be without damage or deterioration (other than normal weathering) at the time of acceptance.

Horton Automatics reserves the right to make product improvements and change specifications without notice.

## END OF SECTION