DIVISION 08 - OPENINGS

SECTION 08 17 00 – INTEGRATED INDUSTRIAL DOOR OPENING ASSEMBLIES

Specifier Note: Coordinate and edit articles and paragraphs below to suit project requirements. Add section numbers and titles per CSI "MasterFormat" and specifier's practice. Consult with manufacturer regarding performance requirements for units applicable to project, as well as related equipment and accessories required.

PART I – GENERAL

1.01 SUMMARY

A. 	WORK INCLUDED: Furnish specified complete automatic industrial door system, that has been manufactured, fabricated & installed to meet manufacturer’s standards without defects, damage, or failure.

B. 	RELATED WORK: Openings: Division 08, applicable sections.

1.02 REFERENCES

A. 	THE ALUMINUM ASSOCIATION (AA) Aluminum Finishes Manual.

B. 	AMERICAN SOCIETY FOR TESTING AND MATERIALS (ASTM) B221: Aluminum-Alloy Extruded Bars, Rods, Shapes and Tubes.

C. 	AMERICAN NATIONAL STANDARDS INSTITUTE (ANSI) Z97.1: Safety Glazing Materials Used in Buildings - Methods of Test.

D. 	INTERTEK, WARNOCK HERSEY (ETL): Testing Laboratory and Certification Agency joined with ETL SEMKO

E. 	UNDERWRITERS LABORATORY, INC. (USA & CANADA) UL 325: Electrical Door, Drapery, Gate, Louver, and Window Operators and Systems.

1.03 SUBMITTALS

A. 	SHOP DRAWINGS & PRODUCT DATA: Submit drawings and product data showing layout, profiles, product components including anchorage, accessories, finish and glazing details (where required).

B. 	CLOSEOUT SUBMITTALS: Owner’s Manual & Warranty document as specified herein.

1.04 QUALITY ASSURANCE AND PERFORMANCE REQUIREMENTS

A. 	INSTALLERS QUALIFICATIONS: Installer shall be factory trained, certified by AAADM, and experienced to perform work of this section.

B. 	MANUFACTURER’S QUALIFICATIONS: Manufacturer to have minimum (5) five years successful experience in the fabrication of automatic doors of the type required for this project. Manufacturer capable of providing field service representation during installation, approving acceptable installer and approving application method.

C.	CERTIFICATIONS: ETL Listed: Tested to UL 325 Standard

D.	OPERATING RANGE: -30° F to 130° F (-34° C to 54° C)

E. 	CLOSING FORCE REQUIREMENTS: Maximum force required to prevent sliding panel from closing = 28 lbf. (124.5 N) Adjustable Reversing Circuit will reopen door unit if closing path is obstructed.

F.	HEADER CAPACITY: Header shall be capable of supporting:

1.	Biparting: Up to 300 lbs. (136 kg) per slide panel over spans up to 16’-0” (4877mm) without intermediate supports.

2.	Single Slide: Up to 500 lbs. (227 kg) per slide panel over spans up to 9’-0” (2743mm) without intermediate supports.

1.05 WARRANTIES

A. 	MANUFACTURER'S WARRANTY: Units to be warranted against defect in material and workmanship for a period of two years from the Date of Substantial Completion. Manufacturer's warranty is in addition to, and not a limitation of, other rights owner may have under Contract Documents.

B. 	DISTRIBUTOR'S WARRANTY: One year warranty: Labor & transportation charges for defective parts replacement.

1.06 PROJECT CONDITIONS

Field Measurements: Verify actual dimensions/openings by field measurements before fabrication and record on shop drawings. Coordinate with fabrication and construction schedule to avoid construction delays.

1.07 DELIVERY, STORAGE AND HANDLING

A. 	ORDERING AND DELIVERY: Comply with factory's ordering instructions and lead time requirements. Delivery shall be in factory's original, unopened, undamaged containers with identification labels intact.

B. 	STORAGE AND PROTECTION: Provide protection from exposure to harmful weather conditions and vandalism.

# PART II – PRODUCTS

2.01 MANUFACTURER

Horton Automatics, a division of Overhead Door Corporation, shall manufacture automatic industrial sliding door(s) of type(s) and size(s) specified on plans and door schedule.

2.02 EQUIPMENT

A. 	MANUFACTURED DOOR UNITS: Shall include operator, header with roller track, carrier assemblies, sliding door panel(s), framing jambs, activation, safety devices and accessories required for complete installation.

1.	Configuration: Single Slide or Biparting

2.	Mounting Type: Surface mounted with sliding panel(s) sliding along wall eliminating need for sidelite.

3. 	Door Type: Type 010: Sliding panel(s) ‘X’ shall slide along interior side.

B.	OPERATOR: The Electric Operating Mechanism shall be HD-Slide® Series 2001 Belt Drive. Maximum current draw shall not exceed 3.15 amps. The heavy-duty operator shall be mounted and concealed within the header.

1. 	Operating force shall be accomplished through a 1/8 HP DC permanent magnet motor with heavy duty worm gear transmission and 1800 RPM working with reinforced drive belt, attached 1/4” thick steel door hangers, and idler pulley (1/4 HP motor required for door panels weighing 500 lbs). Drive belt to be steel reinforced nylon, 1" (25.4 mm) wide. Idler pulley to be reinforced, metallic material.

2.	Microprocessor-based control shall include a 40-character alphanumeric display to provide ease of adjustment and comprehensive diagnostics, including error and alarm logging. All speeds, forces and time delays shall be independently adjustable. Actuating and safety sensors that provide self-monitoring are supported. Supported operating modes include 2-Way Automatic / 1-Way Exit, Full / Reduced Door Opening,

3. 	On/Off Switch shall be supplied. When switched OFF, unit reverts to free manual operation (likewise during electrical power failure).

C. 	Security and Safety Power Fail Options:

1. 	Automatic lock: Automatically locks slide function of door when in closed position. Additional power supply for autolock not acceptable.

a. 	Autolock Fail Secure: If power fails the lock engages.

b. 	Autolock Fail Safe: If power fails the lock disengages.

2. 	Monitored Power Fail Options (battery back-up):

a. 	Software Selectable Power Fail Open: If power fails the door slides open.

b. 	Software Selectable Power Fail Close: If power fails the door slides closed.

3. 	UPS remote mounted battery back-up

D. 	HD-Slide® HEADER: Shall be 6" (152mm) deep by 8" (203mm) high, heavy duty aluminum construction with removable face plate and extruded support brackets for dead load and lateral strength. Optional 18 ga. #4 stainless steel hood/shroud with endcaps.

E. 	CARRIER ASSEMBLIES AND HEADER ROLLER TRACK: Carrier assemblies shall support door panels with minimum four rollers per panel. Rollers will be non-metallic high quality ball bearing wheels 2" (51mm) diameter. Anti-Derailing shall be accomplished by means of a continuous aluminum extrusion full length of slide panel travel. Overhead header roller track shall be continuous aluminum.

F. 	DOOR PANEL: Heavy duty panel shall have a structural core of resin impregnated Kraft honeycomb with 18 gauge galvanized steel skins. Interior framing shall be extruded 6063T-5 anodized extruded aluminum alloy no less than .09” (2mm) thick. The panel shall present a flush appearance with no exposed fasteners. Nominal panel thickness shall be 1-3/4" (44mm). Sliding panel shall be provided with flush pull(s) and shall have concealed bottom guides to stabilize slide travel.

1. 	Optional Finish: #4 brushed stainless steel.

2. 	Optional Vision Lites: 10”-36” (254mm-914mm) Square or rectangular. Glass prep up to 1 ½” (38mm).

3.	Optional Manual MS Lock (net slide reduced by 2 ½” on single slide & 5” on bipart.

a. Hookbolt Latch, 5/8” laminated stainless steel, latching into jamb or adjacent strike rail.

b. Keyed 1 5/32" (29 mm) Cylinder mounted on exterior side with 31/32" (25 mm) backset

c. Thumbturn mounted on interior side.

G. JAMBS/FRAME: Shall be aluminum. Jamb dimensions to be: 1 3/4" (44mm) deep by 4" (102mm) wide.

2.03  RELATED EQUIPMENT

A. ACTIVATING DEVICE: Shall be 24 VDC, class ll circuit. Mounted at interior & exterior for 2-way traffic. Door opens flush with wall opening and closes after time delay expires and slide opening is clear. Actuators can be overhead sensors or jamb mounted pushbuttons or wave sensors (optional wall mounted).

B. 	Threshold presence sensors:

1. 	Header mounted sensors shall provide active infrared presence detection on each side of the door unit and shall remain active throughout the entire door opening and closing cycle.

2. 	Hold-open beams: Two pulsed infrared photoelectric beams to be mounted in vertical rails of sidelite or in jambs. Sender/receiver arrangement parallels door opening.

2.04  RELATED WORK REQUIREMENTS

A. 	ELECTRICAL: 120 VACS, 50/60 cycle, single phase, dedicated 20-amp circuit per operator. Non-North American voltages can be 240 VAC 50/60 cycle (operator must have 240-volt power supply).

B. 	GLASS AND GLAZING: Glass stops, glazing vinyl and setting blocks for field glazing as per Safety Glazing standard ANSI Z97.1.2. Contractor to coordinate acquisition of glass in thickness and type in accordance with manufacturer's recommendations for prescribed design.

2.05  MATERIALS, FINISHES AND FABRICATION

A. 	EXTRUDED ALUMINUM: ASTM B221, 6063-T5 alloy and temper, anodized:

1. 	Structural Header Sections: Minimum 3/16" (5 mm) thickness.

2. 	Structural Frame Sections: Commercial grade.

3.  Structural Panel Sections: Commercial grade.

B. 	FINISHES (for all exposed aluminum surfaces): Shall be one of the following:

1. 	Clear Architectural Class 1 Anodized Coating, AA-MI2C22A41.

2. 	Clad with stainless steel: #4 brushed finish.

C.	PANEL CONSTRUCTION: Corner block type with 3/16" steel backup plate construction, mechanically secured with minimum of four hardened steel screws. Also, refer to Article 2.02, paragraph F. DOOR PANEL

D. 	FRAME CONSTRUCTION: Butt joints, mechanically secured by means of screws & formed aluminum brackets.

E. 	OPERATOR CONSTRUCTION: Electromechanical, modular type construction.

PART III - EXECUTION

3.01 EXAMINATION

Site Verification of Conditions: Installer shall verify base conditions are acceptable for product installation as per manufacturer's instructions. Notify Contractor in writing of conditions detrimental to proper & timely completion of work. All negative conditions to be corrected in a manner acceptable to the manufacturer.

3.02 INSTALLATION

A. 	GENERAL: Installer shall be factory trained, certified and experienced to perform work of this section. Install door units plumb, level and true to line, without warp or rack of frames or sash with manufacturer's prescribed tolerances. Provide support and anchor in place. Provide weather-tight construction.

B. ELECTRICAL: General or electrical contractor to install all wiring to operator on a separate circuit breaker routed into header. General or electrical contractor also to install all necessary power and low voltage wiring for proper operation of associated security systems.

C. 	DISSIMILAR MATERIALS: Comply with AAMA 101, Appendix Dissimilar Materials by separating aluminum materials and other corrodible surfaces from sources of corrosion or electrolytic action contact points.

3.03 CLEANING, ADJUSTMENT AND PROTECTION

A. 	CLEANING AND ADJUSTEMENT: Remove temporary protection of adjacent work areas. Remove construction debris from construction site and legally dispose of debris. Repair or replace damaged installed products. Clean product surfaces and lubricate operating equipment for optimum condition and safety

B. 	ADVISE CONTRACTOR: Of precautions required through the remainder of the construction period, to ensure that doors will be without damage or deterioration (other than normal weathering) at the time of acceptance.

Horton Automatics reserves the right to make product improvements and change specifications without notice.

## END OF SECTION